## Sheet1
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
checked by : |  |  |  | Introduction
The pupose of this Calculation is to design Retaining wall and check the adequecy of this retaining wall
Design by: |  |  | against overturning and sliding forces
Description | Calculation of pier Foundation
Notations :
P= Wheel load
q=Surcharge load
W1: weight of soil above fa part of footing
W2:Weight of Concret pad (footing)
W3: Weight of Retaining wall
Rev.# | Date |  |  |  | W4: Weight of Soil above ct (part footing)
1 | .20/9/07
wt:wall thickness
Ft:Footing thickness
reference : |  |  |  |  | fa:Front part footing width |  |  |  | Figure 1
ct: footing part width
A:Footing length
B:Footing width 1m strip wall
Given Data
Soil &Wall Data
[5 empty] | γs= | 19 | Density of soil |  | kN/m3
[5 empty] | Φ= | 25 | angle friction of soil |  | deg
[5 empty] | ka= | 0.46631 | active earth pressure coefficient
[5 empty] | kP= | 2.4639 | passive earht pressure coefficient
[5 empty] | A= | 2.5 | m
[5 empty] | wt= | 0.3 | m
[5 empty] | fa= | 1.5 | m
[5 empty] | ct= | 0.7 | m
[5 empty] | Hs= | 2.5 | m | backfilling depth behinde the wall
[5 empty] | sd= | 0.6 | m | soil passive pressure depth
[5 empty] | Hw= | 3 | m
[5 empty] | P= | 7.92 | kN | concentrat wheel load
[5 empty] | q= | 0 | kN/m2 | surcharge load
[5 empty] | Ft= | 0.35 | m
Concrete Material Properties:
[5 empty] | fy= | 41.188 | kN/cm2 | yield strength of steel
[5 empty] | fc= | 3.1 | Mpa (kN/cm2) | compressive strength of Concrete
[5 empty] | γs= | 24 | kN/m3 | concrete Density
Job No |  |  | Project titel: |  |  |  |  | Contractor :
SSEM
plant Number
Designer Office
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
checked by : |  |  |  | Precast Wall Data
Design by: |  |  |  | Hp= | 3.25 | m | hight of precast wall
|  |  |  | THp= | 0.12 | m | thickness of precast wall
Description | Calculation of pier Foundation | 0
Loads :
|  |  | Code | Vertical Loads
|  |  | 1 | W1= | 71.25 | kN/m` | weight of soil at fa width
|  |  | 1 | W2= | 21 | kN/m` | weight of footing
|  |  | 1 | W3= | 21.6 | kN/m` | weight of retaining wall
|  |  | 1 | W4= | 7.98 | kN/m` | weight of soil at ct width
|  |  | 1 | W5= | 9.36 | kN/m` | weight of precast wall
Rev.# | Date |  | 1 | q= | 11.8 | kN/m2 | surcharge loads |  | as per AASHTO page 27
1 | .20/9/07 |  | 1 | P= | 7.92 | kN | wheel loads
0 | 0
0 | 0
0 | 0 |  |  | Horizontal Loads
0 | 0
|  |  | Code: | Horizontal Pressure of soil and the surcharge
|  |  | 1 | Pa1= | 22.1496 | kN/m`
|  |  | 1 | Pa2= | 3.1009 | kN/m`
|  |  | 0 | PP1= | 28.0886 | kN/m`
|  |  | 0 | PP2= | 16.385 | kN/m`
|  |  | 1 | Ps= | 5.5024 | kN/m`
|  |  | 1 | Psw= | 7.92 | kN/m`
Wind Load:AS per UBC97 code
Basic wind speed
|  |  |  | Wis= | 150 | km/h
Pw=wind stagnation pressure
|  |  |  | Pw= | 22.3 | psf
[5 empty] | 1.07 | kPa | 108kg/m2
hieght above average level of adjoining Ground
|  |  |  | H= | 3.25 | m
Ppw=Ce*Cq*Iw*Pw
|  |  |  | Ce= | 1.06 | Combined height ,Exposure and gust factor coeff.
|  |  |  | Cq= | 1.3 | Pressure coefficient for retaining wall
|  |  |  | Iw= | 1.15 | Important Factor (occupancy structur)
|  |  |  | Ppw= | 5.1503 | kN/m2 | Force Due to wind
Job No | [7 empty] | Contractor :
SSEM
plant Number
Designer Office
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
checked by :
Table of loads and Moments affecting on the Retaning Wall
Design by:
Description | Calculation of pier Foundation | 0 | Codes | Loads name | Loads | lever Arm | Moment
[5 empty] | kN | m | kN.m
|  |  | 1 | W1= | 71.25 | 1.75 | 124.6875 |  | Resistance to Ovt.moment
|  |  | 1 | W2= | 21 | 1.25 | 26.25 |  | Resistance to Ovt.moment
|  |  | 1 | W3= | 21.6 | 0.85 | 18.36 |  | Resistance to Ovt.moment
|  |  | 1 | W4= | 7.98 | 0.35 | 2.793 |  | Resistance to Ovt.moment
|  |  | 1 | W5= | 9.36 | 0.85 | 124.6875 |  | Resistance to Ovt.moment
|  |  | 1 | PS= | 13.7561 | 1.1833 | 16.278 |  | Ovt.moment
|  |  | 1 | Pa1= | 3.8762 | 1.1833 | 4.5868 |  | Ovt.moment
|  |  | 1 | Pa2= | 0.54267 | 0.11667 | 0.063311 |  | Ovt.moment
|  |  | 1 | Ppw= | 16.7384 | 4.625 | 77.4151 |  | Ovt.moment
|  |  | 0 | Pp1= | 0 | 0.2 | 0 |  | Resistance to Ovt.moment
Rev.# | Date |  | 0 | Pp2= | 0 | 0.11667 | 0 |  | Resistance to Ovt.moment
|  |  | 1 | Psw= | 9.9 | 1.6 | 15.84 |  | Ovt.moment
[5 empty] | SF.ovt= | 2.5991 | >2 ok | Sfovt=R.Ovt.Mom/Ovt.Mom
[5 empty] | SF.slid= | 1.2053 | Recheck
Design of Retaining Wall:
|  |  |  | loads name | Load | lever Arm | moment
|  |  |  | Ps= | 13.7561 | 1.25 | 17.1951
|  |  |  | Pa1= | 3.8762 | 0.83333 | 3.2302
|  |  |  | Ppw= | 16.7384 | 4.625 | 77.4151
|  |  |  | Pp1= | 0 | 0.2 | 0
|  |  |  | Pp2= | 0 | 0.11667 | 0
|  |  |  | Psw= | 9.9 | 1.25 | 12.375 | kN.m
|  |  |  | Total Moment acting on the wall |  |  | 110.2153
|  |  |  | Vertical loads= |  | 30.96 | kN | from the moment and vertical load steel can obtain by
PCACOL
|  |  |  | Mu=1.3*M |  |  | 16.0875 | kN.m
|  |  |  | H= | 300 | mm
|  |  |  | d` | 75 | mm | Steel Cover
|  |  |  | d= | 217 | mm
|  |  |  | Φ= | 0.9 |  | strip from the boundary wall
|  |  |  | b= | 1000 | mm
|  |  |  | R=Mu/(Φ*b*d^2) | 0.3796 |  |  | fy= | 4200 | kg/cm2
|  |  |  | m=fy/(0.85fc) | 17.6471 |  |  | fc= | 280 | kg/cm2
|  |  |  | ρ=(1/m)*((1-(1-2*R*m/fy)^0.5) |  |  |  |  | 17.6471
ref.ACI -318-08 |  |  |  | ρ= | 0.00056576 |  | ρmin= | 0.0015 | AS per ACI-318 -02 clause 14.3.2
cls. 14.3.2
Job No |  |  | Project titel: |  |  |  |  | Contractor :
SSEM
plant Number
Designer Office
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
Vertical Main Bars:
checked by : |  |  |  | As= | 325.5 | mm2 |  | Φd=12mm | 12
Vertical steel Area Required
Design by:
Description | Calculation of pier Foundation | 0
Horizontal Bar:
|  |  |  | ρmin= | 0.002 | as per ACI 318 Cluase 14.3.3
|  |  |  | ASh= | 600 | mm2
ref to ACI-318 cluase 14.3.4 when wall thickness more than 25cm tow layer of steel should be used
1/2 < steel required for each face>2/3 of the Required Steel
Rev.# | Date
|  |  |  | Av= | 217 | mm2 | Area of steel required for each vertical layer
|  |  |  | Nbv= | 1.9188 | number of bar in each layer
|  |  |  | Then Chose 12mm@250mm |  |  | Tow layer for Virtical bars
|  |  |  | Ash=2/3xAv | 400 | mm2 | steel Required For each horizontal layerd
|  |  | cot(phI) |  | 0
|  |  | tan(45+phi/2)^2= | Nhb= | 3.5368 | nomber of bars in each layer
|  |  | e^(3.141592*tan(phi)= |  | 1
|  |  | 0 | Then chose 12mm@250mm
1
Design of shear on the Wall
|  |  |  | Shear force= | 34.9133 | kN | maximum Shear Force at the base of wall
ΦVc=(1/6)*Φ*(fc^0.5)*b*d)
|  |  |  | ΦVc= | 704.3726 | kN | Then no need for shear Reinforcement
Job No |  |  | Project titel: |  |  |  |  | Contractor :
SSEM
plant Number
Designer Office
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
checked by : |  |  |  | Design of Footing of The Wall
Design by:
Description | Calculation of pier Foundation | 0
|  |  |  | P= | 131.19 | kN | Vertical Load Acting on Footing
Calculate the moment acting at the base of footing
|  |  | Code | L.Name | Load kN | Arm lever | Moment
|  |  | 1 | W1= | 71.25 | 0.5 | 35.625
|  |  | 1 | W2= | 21 | 0 | 0
|  |  | 1 | W3= | 21.6 | -1.1 | -23.76
|  |  | 1 | W4= | 7.98 | -0.9 | -7.182
|  |  | 1 | W5= | 9.36 | -0.49 | -4.5864
|  |  | 0 | PS= | 0 | 2.85 | 0
|  |  | 1 | Pa1= | 3.8762 | 1.1833 | 4.5868
|  |  | 1 | Pa2= | 0.54267 | 0.11667 | 0.063311
Rev.# | Date |  | 1 | Ppw= | 16.7384 | 4.625 | 77.4151
|  |  | 0 | Pp1= | 0 | -0.55 | 0
|  |  | 0 | Pp2= | 0 | -0.11667 | 0
|  |  | 1 | Psw= | 9.9 | 1.6 | 15.84
|  |  | Total moment acting on base footing. |  |  | ΣMb= | 98.0018 | kN.m
|  |  |  | A= | 2.5 | m | length of footing
|  |  |  | B= | 1 | m | width of footing
|  |  |  | BC= | 200 | kN/m2 | net bearing capacity
|  |  |  | Ix= | 1.3021 | m4
|  |  |  | Iy= | 0.20833 | m4
σ1=P/A+( Mx/Ix)y +(My/Iy)x
σ2=P/A-( Mx/Ix)y -(My/Iy)x
σ3=P/A+( Mx/Ix)y -(My/Iy)x
σ4=P/A-( Mx/Ix)y +(My/Iy)x
Job No |  |  | Project titel: |  |  |  |  | Contractor :
SSEM
plant Number
Designer Office
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
checked by : |  |  |  | Lateral pressure due to surcharge Load
Design by: |  |  |  | P= Nearest Wheel load
Description | Calculation of pier Foundation | 0
|  |  |  | P | 16 | kips
|  |  |  | x= | 2 | ft
|  |  |  | H= | 8.36 | ft
|  |  |  | m=x/h | 0.23923
n=Z/H
Rev.# | Date
m>0.4
m<0.4
|  |  |  | n= | m= | δ=
|  |  |  | 0 | 0.23923 | 0
|  |  |  | 0.1 | 0.23923 | 0.13047
|  |  |  | 0.2 | 0.23923 | 0.32051
|  |  |  | 0.3 | 0.23923 | 0.36922
|  |  |  | 0.4 | 0.23923 | 0.31299
|  |  |  | 0.5 | 0.23923 | 0.23252
|  |  |  | 0.6 | 0.23923 | 0.16412
|  |  |  | 0.7 | 0.23923 | 0.11437
|  |  |  | 0.8 | 0.23923 | 0.080126
|  |  |  | 0.9 | 0.23923 | 0.05689
|  |  |  | 1 | 0.23923 | 0.041067
|  |  |  | average δ= | 0.16566 | kip/ft2
|  |  |  | Or δd= | 7.92 | kPa
Job No |  |  | Project titel: |  |  |  |  | Contractor :
SSEM
plant Number
Designer Office
Approved by |  |  | SAUDI ELECTRICAL COMPANY- EOA
checked by :
Design by:
Description | Calculation of pier Foundation
Rev.# | Date
Job No |  |  | Project titel: |  |  |  |  | Contractor :
SSEM
plant Number
Designer Office
Note on K42: Engr. Hakim: angle are in radian so check
Note on N215: Engr. Hakim: calculating nc1
Note on F112: Hakim: or 1.15
Note on F168: Hakim: 300-75-dia/2
Note on E199: Hakim: 1check aci 318 cluase 14.3.3 & 14.3.4
Note on E93: Hakim: pressure Due to wheel load
Note on F81: Hakim: check this load belong to which case edge base or above base footing